{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":31,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":48,"n_cols":3,"rows_kept":48,"cut":false,"hidden":false,"merged":[[47,0,47,1]]}
["PFCS Calculator","Ver. 6 (6-Apr-2021)"]
[]
["Power Supply"]
["Output Voltage (V)",57,"PsRatedVout"]
["Output Power (W)",100,"PsRatedPout"]
[]
["Powered Fiber Cable"]
["Conductor Gauge (AWG)","12 AWG","PfcAWG"]
["Ambient Temp (C)","55C (Sunlight Exposed)","PfcTemp"]
[]
["Extender","1-port 1Gb PoE PFU-P-C-O-060-01","ExtenderType"]
[]
["Cable Length Units","Meters","Units"]
[]
["Powered Device #1"]
["PoE Device Class","Class 6","PdClass1"]
["Max Input Power (W)",51,"PdMaxPwrSpec1"]
["Min Input Voltage (V)",42.5,"PdMinVinSpec1"]
["Max Input Voltage (V)",57,"PdMaxVinSpec1"]
["Cable Type","CS Cat6a F/UTP Outdoor Patch Cord (Recommended)","PdCableType1"]
["Cable Ambient Temp","55C (Sunlight Exposed)","PdCableTemp1"]
[{"$f":"\"Cable Length (\" & IF(Units=\"Meters\",\"m\", \"ft\") & \")\"","v":"Cable Length (m)"},50,"PdCableLength1"]
[]
["Powered Device #2"]
["Powered Device Class","Not applicable","PdClass2"]
["Max Input Power (W)","Not applicable","PdMaxPwrSpec2"]
["Min Input Voltage (V)","Not applicable","PdMinVinSpec2"]
["Max Input Voltage (V)","Not applicable","PdMaxVinSpec2"]
["Cable Type","Not applicable","PdCableType2"]
["Cable Ambient Temp","Not applicable","PdCableTemp2"]
[{"$f":"\"Cable Length (\" & IF(Units=\"Meters\",\"m\", \"ft\") & \")\"","v":"Cable Length (m)"},"Not applicable","PdCableLength2"]
[]
["Result"]
[{"$f":"\"Powered Fiber Cable max length (\" & IF(Units=\"Meters\",\"m\", \"ft\") & \")\"","v":"Powered Fiber Cable max length (m)"},780.9089078138727,"PfcMaxLength"]
[]
["Additional Information"]
["Worst case supply output current (A)",1.6945696472191556,"PsIout"]
["Worst case supply output power (W)",96.590469891491864,"PsPout"]
["Extender minimum input voltage (V)",41.312426075501293,"ExtenderMinVin"]
["Extender minimum output voltage (V)",50,"ExtenderMinVout"]
["Port 1 maximum output current (A)",1.0825193857373223,"ExtenderMaxIout1"]
["Port 1 maximum output power (W)",54.125969286866116,"ExtenderMaxPout1"]
["Port 1 powered device input voltage (V)",47.112320270609324,"PdMinVin1"]
["Port 2 maximum output current (A)","Not applicable","ExtenderMaxIout2"]
["Port 2 maximum output power (W)","Not applicable","ExtenderMaxPout2"]
["Port 2 powered device input voltage (V)","Not applicable","PdMinVin2"]
[]
["DISCLAIMER: These calculations are provided for guidance purposes only. They are provided “as is” and should not be relied upon without consultation with and supervision of experienced personnel and a local CommScope representative. CommScope makes no representations or warranties of any kind related to these tools, whether express or implied, and specifically disclaims and excludes any representation or warranty of merchantability, quality, content, completeness, suitability, adequacy, accuracy, noninfringement or fitness for a particular purpose and any representation arising by usage of trade, course of dealing or course of performance. CommScope is under no obligation to issue any upgrades, update specifications or notify users of this tool that changes have been made. The user of these tools assumes all risks associated with such use, and CommScope hereby disclaims any and all liability for damages of any kind resulting from such use."]