## Instructions
CommScopeDistance Calculator for PoE/Power Extenders
→ Set the Design Parameters needed in the Yellow Cells
→ Results based on Design Parameters are provided in the Tan Cells
DISCLAIMER: These calculations are provided for guidance purposes only. They are provided “as is” and
should not be relied upon without consultation with and supervision of experienced personnel and a
local CommScope representative. CommScope makes no representations or warranties of any kind related
to these tools, whether express or implied, and specifically disclaims and excludes any representation
or warranty of merchantability, quality, content, completeness, suitability, adequacy, accuracy,
noninfringement or fitness for a particular purpose and any representation arising by usage of trade,
course of dealing or course of performance. CommScope is under no obligation to issue any upgrades,
update specifications or notify users of this tool that changes have been made. The user of these tools
assumes all risks associated with such use, and CommScope hereby disclaims any and all liability for
damages of any kind resulting from such use.
Contact CommScope Systems Engineering for help with powered fiber calculations
that do not involve the PFU line of PoE and power extenders.
Voltage, Current, and Power results are based on minimum Extender performance
and actual results may be different.
Version 10

## PFU-P-C-O-090-02
FiberREACH PoE Class 8 Extender PFU-P-C-O-090-02
Power Supply |  | Parameters based on CLASS
Supply Voltage (25-57V) | 57 | #Cond | Pmax | MAX PoE Length based on type
Supply Power (≤100W) | 100 | 8 | 71.3 | LmaxSUN | LmaxDuct | Lmax | Lmax
|  |  |  | 78 | 83 | 78 | 78
Port 1 |  |  | CableP | Temperature | Rloop
PoE Device Class | Class8 |  | 0.0938 | 55 | 0.16005
Device Power | 71.3
Cable Length Units | Meters
Cable Type | CS Cat6a F/UTP Outdoor Cord (Recommended) | #Cond | Pmax | MAX PoE Length based on type
Cable Ambient Temp | 55C (Sunlight Exposed) | 4 | 6.49 | LmaxSUN | LmaxDuct | Lmax | Lmax
Cable Length up to 78m | 3 |  |  | 78 | 83 | 78 | 78
Port 2
PoE Device Class | Class2 |  | CableP | Temperature | Rpoe
Device Power | 6.49 |  | 0.0938 | 55 | 0.32011
Cable Length Units | Meters
Cable Type | CS Cat6a F/UTP Outdoor Cord (Recommended) |  | PoE Load calculations
Cable Ambient Temp | 55C (Sunlight Exposed) |  | VminPd | VminXo | ImaxXo | PmaxXo | PFC loop calculations
Cable Length up to 78m | 3 |  | 51.7796 | 52 | 1.377 | 71.6035 | PmaxXi
|  |  | VminPd | VminXo | ImaxXo | PmaxXo | 91.4815
FiberREACH Powered Fiber Cable |  |  | 51.96 | 52 | 0.1249 | 6.495
Ambient Temperature | 55C (Sunlight Exposed) | AWG | Temp | P | Rcable0 | Rcable1 | Rlmax
PF Cable Guage | 12 AWG | 12 | 55 | 0.0052107 | 8.8788 | 2.7677 | 2.6293
PF Cable Length (meters) | 222 |  |  |  |  | Vx | 52.4106
PF Cable Length (feet) | 728 |  |  |  |  | Ix | 1.7455
PF Cable Resistance Ω | 2.6293 |  | 221.7901 |  |  | Ps | 99.4921
Supply Current (Amps) | 1.7455 |  | 727.658 |  |  | Pcable | 8.0106
Supply Power (Watts) | 99.4921

## PFU-P-C-O-060-02
FiberREACH PoE Class 4 Extender PFU-P-C-O-060-02
Power Supply |  | Parameters based on CLASS
Supply Voltage (25-57V) | 57 | #Cond | Pmax | MAX PoE Length based on selection parameters
Supply Power (≤100W) | 100 | 4 | 25.5 | LmaxSUN | LmaxDuct | Lmax | Lmax
Port 1 |  |  |  | 78 | 83 | 78 | 78
PoE Device Class | Class4 |  | CableP | Temperature | Rloop
Device Power | 25.5 |  | 0.0938 | 55 | 0.32011
Cable Length Units | Meters
Cable Type | CS Cat6a F/UTP Outdoor Cord (Recommended) | #Cond | Pmax | MAX PoE Length based on selection parameters
Cable Ambient Temp | 55C (Sunlight Exposed) | 4 | 25.5 | LmaxSUN | LmaxDuct | Lmax | Lmax
Cable Length up to 78m | 3 |  |  | 78 | 83 | 78 | 78
Port 2
PoE Device Class | Class4 |  | CableP | Temperature | Rpoe
Device Power | 25.5 |  | 0.0938 | 55 | 0.32011
Cable Length Units | Meters
Cable Type | CS Cat6a F/UTP Outdoor Cord (Recommended) |  | PoE Load calculations
Cable Ambient Temp | 55C (Sunlight Exposed) |  | VminPd | VminXo | ImaxXo | PmaxXo | PFC loop calculations
Cable Length up to 78m | 3 |  | 49.8362 | 50 | 0.51168 | 25.5838 | PmaxXi
|  |  | VminPd | VminXo | ImaxXo | PmaxXo | 66.645
FiberREACH Powered Fiber Cable |  |  | 49.8362 | 50 | 0.51168 | 25.5838
Ambient Temperature | 55C (Sunlight Exposed) | AWG | Temp | P | Rcable0 | Rcable1 | Rlmax
PF Cable Guage | 12 AWG | 12 | 55 | 0.0052107 | 12.1877 | 10.837 | 10.2952
PF Cable Length (meters) | 868 |  |  |  |  | Vx | 39.7383
PF Cable Length (feet) | 2849
PF Cable Resistance Ω | 10.2952 |  | length |  |  | Ix | 1.6767
Supply Current (Amps) | 1.6767 |  | 868.4364 |  |  | Ps | 95.5707
Supply Power (Watts) | 95.5707 |  | 2849.201 |  |  | Pcable | 28.9424

## PFU-P-C-O-060-01
FiberREACH PoE Class 6 Extender PFU-P-C-O-060-01
Power Supply |  | Parameters based on CLASS
Supply Voltage (25-57V) | 57 | #Cond | Pmax | MAX PoE Length based on selection parameters
Supply Power (≤100W) | 100 | 4 | 25.5 | LmaxSUN | LmaxDuct | Temp | UNITS
|  |  |  | 78 | 83 | 78 | 78
Powered Device
PoE Device Class | Class4
Input Power | 25.5
Cable Length Units | Meters | CableP | Temperature | Rpoe
Cable Type | CS Cat6a F/UTP Outdoor Cord (Recommended) | 0.0938 | 55 | 5.3351
Cable Ambient Temp | 55C (Sunlight Exposed)
Cable Length up to 78m | 50
FiberREACH Powered Fiber Cable |  |  | PoE Load calculations |  |  |  | PFC loop calculations
Ambient Temperature | 55C (Sunlight Exposed) |  | VminPd | VminXo | ImaxXo | PmaxXo | PmaxXi
PF Cable Guage | 12 AWG |  | 47.1123 | 50 | 0.54126 | 27.063 | 39.2534
PF Cable Length (meters) | 1658 | AWG | Temp | P | Rcable0 | Rcable1 | Rlmax
PF Cable Length (feet) | 5440
PF Cable Resistance Ω | 19.6579 | 12 | 55 | 0.0052107 | 20.6925 | 19.7366 | 19.6579
Supply Current (Amps) | 1.1248 |  |  |  |  | Vx | 34.8879
Supply Power (Watts) | 64.1163 |  |  |  |  | Ix | 1.1248
NOTE: Only Supports Dual Signature Detection for Class 5 & 6 Devices |  |  | 1658.2124 |  |  | Ps | 64.1163
|  |  | 5440.3295 |  |  | Pcable | 24.8727

## PFU-48-C-O-060-01
FiberREACH 48V Extender PFU-48-C-O-060-01
Power Supply
Supply Voltage (25-57V) | 57 | Find Maximum Pd cable length
Supply Power (≤100W) | 100 | Rcable0 | Rcable1 | Rlmax | Max Length | Vpd
|  | 0.97872 | 7.9769 | 0.97872 | 20.5363 | 46.0003
Powered Device
Device Power (1-60W) | 47
Min Device Voltage (≤47.0V) | 46
Cable Length Units | Meters | PdCable AWG | PdCableP | Pd cable T | Rloop
Cable Type | 18 AWG | 18 | 0.020948 | 55 | 0.95317
Cable Ambient Temp | 55C (Sunlight Exposed)
Cable Length up to 20m | 20
Cable Resistance Ω | 0.95317 | Find Maximum PFC length
|  |  | VminXo | VminPd | ImaxXo | PmaxXo | PmaxXi
FiberREACH Powered Fiber Cable |  |  | 47 | 46.0267 | 1.0211 | 47.9939 | 63.0385
Ambient Temperature | 55C (Sunlight Exposed) | AWG | Temp | Rlmax | Rcable0 | Rcable1 | P
PF Cable Guage | 12 AWG | 12 | 55 | 11.4083 | 12.885 | 12.0088 | 0.0052107
PF Cable Length (meters) | 962
PF Cable Length (feet) | 3157
PF Cable Resistance Ω | 11.4083 |  |  |  |  | Vx | 38.148
Supply Current (Amps) | 1.6525 |  | 962.3357 |  |  | Ix | 1.6525
Supply Power (Watts) | 94.1908 |  | 3157.2694 |  |  | Ps | 94.1908
Powered Device Voltage | 46.0267 |  |  |  |  | Vpd | 46.0267
Powered Device Current | 1.0211

## PFU-12-C-O-060-01
FiberREACH 12V Extender PFU-12-C-O-060-01
Power Supply
Supply Voltage (25-57V) | 57 | Find Maximum Pd cable length
Supply Power (≤100W) | 100 | Rcable0 | Rcable1 | Rlmax | Max Length |  | Vpd
|  | 0.68906 | 0.6125 | 0.6125 | 12.8519 |  | 7.0017
Powered Device
Device Power (1-60W) | 40
Min Device Voltage (≤10.5V) | 5
Cable Length Units | Meters | PdCable AWG | PdCableP | Pd cable T | Rloop
Cable Type | 18 AWG | 18 | 0.020948 | 55 | 0.5719
Cable Ambient Temp | 55C (Sunlight Exposed)
Cable Length up to 12m | 12 | Find Maximum PFC length
Cable Resistance Ω | 0.5719
|  |  | VminXo | VminPd | ImaxXo | PmaxXo | PmaxXi
FiberREACH Powered Fiber Cable |  |  | 10.5 | 7.4148 | 5.3946 | 56.6432 | 72.8673
Ambient Temperature | 55C (Sunlight Exposed) | AWG | Temp | Rlmax | Rcable0 | Rcable1 | P
PF Cable Guage | 12 AWG | 12 | 55 | 8.3746 | 11.147 | 8.8154 | 0.0052107
PF Cable Length (meters) | 706
PF Cable Length (feet) | 2318 | Ω | length |  |  | Vx | 42.7131
PF Cable Resistance Ω | 8.3746
Supply Current (Amps) | 1.706 |  | 706.4323 |  |  | Ix | 1.706
Supply Power (Watts) | 97.2403 |  | 2317.6914 |  |  | Ps | 97.2403
Powered Device Voltage | 7.4148 |  |  |  |  | Vpd | 7.4148
Powered Device Current | 5.3946

## Powered Fiber Cable (hidden)
Length to User Device (5% Margin applied)
Power Supply |  | Just PFC to some other powered device (no Extender)
Supply Voltage | 57
Supply Power | 100 | AWG | Temp | Rlmax | Rcable0 | Rcable1 | P
End User Powered Device |  | 12 | 55 | 15.4327 | 16.245 | 16.245 | 0.0052107
Min Device Voltage ≤57V | 10 |  | Vx | 34.8728 | 28.5014 | 28.5014
Device Power ≤100W | 50 |  | Ix | 1.4338 | 1.7543 | 1.7543
|  |  | Ps | 81.7256 | 99.995 | 99.995
FiberREACH Powered Fiber Cable |  |  |  | V-Limited | V-Limited | P-Limited
Ambient Temperature | 55C (Sunlight Exposed) |  | Crosscheck on power splits
PF Cable Guage | 12 AWG |  | V | I | P | Ptotal
PF Cable Length (meters) | 1302 | PFC | 22.1272 | 1.4338 | 31.7256
PF Cable Length (feet) | 4271 | Pd | 34.8728 | 1.4338 | 50 | 81.7256
PF Cable Resistance Ω | 15.4327
Device Voltage (V) | 34.8728
Supply Current (Amps) | 1.4338 |  | Length
Supply Power (Watts) | 81.7256 |  | 1301.8092
4271.0277
Alternate Calculation - Highest Available Power (no 5% Margin)
Length and Minimum Voltage INPUT
Power Supply
Supply Voltage | 57 |  | AWG | Temp | P | Rlength | R
Supply Power | 100 |  | 12 | 55 | 0.0052107 | 15.435 | 15.435
FiberREACH Powered Fiber Cable |  |  |  | Rcable0 | Rcable1 |  | MinDeviceVoltage
Ambient Temperature | 55C (Sunlight Exposed) |  |  | P of V | P for lim-p | V&Plimited | pofVmin
PF Cable Guage | 12 AWG |  | Pd | 49.995 | 52.493 | 52.493 | 49.995 | 49.995
Cable Length Units | Meters |  | Vd | 34.87 | 29.921 | 29.921 | 34.87 | 34.87
PF Cable Length (Meters) | 1302
|  |  | Pr | 31.729 | 15.435 | 15.435 | 31.729 | 31.729
End User Device Power |  |  | Vr | 22.13 | 27.079 | 27.079 | 22.13 | 22.13
Min Device Voltage ≤57V | 34.87
Available Device Voltage | 34.87 |  | Ir | 1.4338 | 1.7544 | 1.7544 | 1.4338 | 1.4338
Available Device Power | 49.995 |  | Ps | 81.7239 | 100 | 100 | 81.7239 | 81.7239
PF Cable Resistance Ω | 15.435 |  |  | V-limited | P-limited | P-limited | D-limited | D-limited
Supply Power (Watts) | 81.7239